# Foundation & Column Shop Drawing — Standby Generator Plinth (Footing G-04 / Column G-02)

Submittal No: DC1-02-SD-0187-R0    Rev: R0    Discipline: Structural

Project: DC1 — Hyperscale Data Centre, Chennai · 48 MW · Tier III (N+1)

Contractor: Sterling & Wilson (Electrical) / L&T Construction (Civil)

This shop drawing covers the reinforced-concrete plinth and support column for the standby generator plant referenced in DC1-16-DBR-0201 (Electrical) and tracked as DC1-04-EL-020 on the project schedule. Structural basis follows the primary Design Basis Report DC1-02-DBR-0001.

## General Notes

General Note 1: Nominal cover to reinforcement for the standby generator plinth footing G-04, severe exposure, is specified as 35 mm.

General Note 2: Longitudinal reinforcement for column G-02 is provided at 1.2 percent.

General Note 3: Formwork for the plinth shall not be struck before 7 days per the primary Design Basis Report's curing schedule.

Prepared by: L&T Construction Structural Design Office

For review against DC1 Compliance Agent baseline checks.