# Design Basis Report Addendum — Standby Generator Earthing & LV Distribution

Submittal No: DC1-16-DBR-0201-R0    Rev: R0    Discipline: Electrical

Project: DC1 — Hyperscale Data Centre, Chennai · 48 MW · Tier III (N+1)

Contractor: Sterling & Wilson (Electrical) / L&T Construction (Civil)

This addendum extends DC1-02-DBR-0001 to cover the earthing and low-voltage distribution basis for the 2N standby generator plant (feeding DC1-04-EL-020, DRUPS 2.5MW) and its associated switchroom, ahead of the L1 factory acceptance test. It should be read together with the primary Design Basis Report.

## General Notes

General Note 1: The standby generator frame is earthed by 1 distinct connection with earth, run in 70 sq mm copper conductor to the yard earth grid.

General Note 2: The standby generator neutral point is earthed by 1 separate connection to the yard earth grid, pending installation of a second independent conductor.

General Note 3: The measured earth grid resistance at the generator yard is 2.5 ohm.

General Note 4: Socket-outlet circuits in the generator control room are protected by a residual current device rated at 25 mA.

General Note 5: All cable containment in the generator switchroom shall be hot-dip galvanised per the primary Design Basis Report's General Note 5 conventions.

Prepared by: Sterling & Wilson Electrical Design Office

For review against DC1 Compliance Agent baseline checks.